  - INTRODUCTION

First of all, thank you for purchasing MyZx series redundant power supply.

The MyZx series is a N+1 hot-swappable / hot-pluggable redundant power supply. It consists of,

The total output is up to your power’s requirements, you can figure out the total

Power’s consumption and check over the specification, the you can find out the correct configuration.

It delivers full safety redundant (hot-swappable) function and provides the hot-pluggable feature. In other words, it can offer a more reliable and safer, easy install / maintain operation in the power energy supply to your system.

Its major function is to deliver the full power and the mean time these power modules can mutually backup once one of the power modules is defective.

It provides a warning subsystem, include LED display, buzzer alarm, TTL signal etc.,

at the same time, it also indicates the status of the power system.

When all the power modules are at normal condition, it balances the load share and results the power system increase reliability.

To really discover the power and ease in using the product, we recommend that

you read through this manual carefully.

  - PACKING

Your MyZx package should consist of the followings:

- MyZx series x 1

- Accessory pack x 1

- Product Manual x 1

  - MODEL DESINGATION

Model number identification

X  X  Y  Z  X – X  XXX  X  X  X

1  2  3  4  5   6   7    8  9  10

1st --- Category

X --- blank AC input ( AC – DC )

D  -48Vdc input

B  -24Vdc input

2nd --- Serial ID

# X --- R  redundant 1 + 1

## M  redundant N + 1

3rd --- for # U use

Y --- 1   for 1U use

- for 2U use

4th --- PM or Customer specify

5th --- # of power module in N+1 system

X --- 1  single

- 1+1 power system

- 2+1 power system

- 3+1 power system

6th --- # of the channel

X --- 2   5V, 12V  ( Disk Array )

4   5V, 12V, -5V, -12V ( AT )

5   5V, 12V, 3.3V, 5Vsb, -12V ( ATX / EPS )

6   5V, 12V, 3.3V, 5Vsb, -5V, -12V ( ATX / EPS )

7th --- # of total wattages

# XXX --- 460

# AXX --- 10XX

# BXX --- 11XX

# CXX --- 12XX

………

8th --- attribute

# X --- P   w/ PFC

## F   w/ EMI filter

V   HIGH EFFICIENCY

9th --- chassis type

# X --- H   horizontal type

V   vertical type

M   horizontal + vertical type

10th --- Use FAN type

X --- 3   use 3.8CM type

- use 4CM type

6   use 6CM type

8   use 8CM type

  - FEATURES

MyZx

N+1, Hot-swap, Hot-plug, AC input min redundant power system

- Low profile power module for building to the requirement

- N+1 power system design

- Current sharing design

- Remote sensing design

- 5 channels ( 5/12/-5/-12/3.3/5Vsb ) 350W /400W / 460W /500W/ 550W power module outputs

- Active power factor correction (PFC) built-in

- Universal AC power input

- Warning methods---LED, buzzer. TTL signal

- UL, UL+C, TUV, CB approved

- Meet FCC class B, CISPR 22 class B

- Truly redundant feature design

- Debounce power disturbance keep from shut-down / reset

- Isolated fence in power housing meets the safety regulation

- Double protection on OCP & OVP

- I2C function (optional)

  - DRAWING

  - SPECIFICATIONS

INPUT CHARACTERISTICS:		    M1Z2-5400V3V/5500V3V/5550V3V

- VOLTAGE: 90 ~ 264 VAC FULL RANGE.

- FREQUENCY: 47 ~ 63 Hz.

- INPUT CURRENT: 3.0 / 4.0 / 4.0 A (RMS) FOR 230 VAC

- 6.0 / 8.0 / 8.0A (RMS) FOR 115 VAC

- INRUSH CURRENT: 35A MAX. FOR 115 VAC PER MODULE

- 40A MAX. FOR 230 VAC PER MODULE

- POWER FACTOR CORRECTION: PFC CAN REACH THE TARGET OF 95% AT 230V, FULL LOAD

- OUTPUT CHARACTERISTICS:

| OUTPUT VOLTAGE | OUTPUT CURRENT(A) |  | REGULATION |  | OUTPUT RIPPLE & NOISE MAX.[P-P] |
| --- | --- | --- | --- | --- | --- |
|  | MIN. | MAX. | LOAD | LINE |  |
| +5V | 0.5 | 24 | ±5% | ± 1% | 70mV |
| +12V | 1.0 | 32/36/45 | ±5% | ± 1% | 120mV |
| -12V | 0 | 0.8 | ±5% | ± 1% | 120mV |
| +3.3V | 0 | 24 | ±5% | ± 1% | 70mV |
| +5VSB | 0 | 3.5 | ±5% | ± 1% | 70mV |

SPECIFICATION:

- TEMPERATURE RANGE: OPERATING 0℃ --- 50℃, STORAGE –20℃ --- 80℃

- HOLD UP TIME: 16 ms MINIMUM AT FULL LOAD & NORMAL INPUT VOLTAGE

- EFFICIENCY: 78% TYPICAL AT 115VAC, FULL LOAD

- POWER GOOD SIGNAL: ON DELAY 100 ms TO 500 ms, OFF DELAY 1 ms

- OVER POWER PROTECTION: 110~160%

- OVER VOLTAGE PROTECTION: +5V→5.7V~6.5V, +3.3V→４.0~5.7V, +12V→14.3~17.3V

- OVER CURRENT PROTECTION

- SHORT CIRCUIT PROTECTION: +5V, +3.3V, +12V, -12V, +5VSB

- SAFETY: TO MEET UL, TUV, CB

- EMI NOISE FILTER: FCC CLASS A, CISPR22 CLASS A

- DIMENSION: 265 (D) x 101 (W) x 84 (H) mm

# INPUT CHARACTERISTICS:		         	M1Z3-6760P3V / M1Z3-6800P3V

- VOLTAGE:  90V ~ 264VAC

- FREQUENCY: 47Hz ~ 63Hz

- INPUT CURRENT: 20-10A MAX AT ANY LOW/HIGH INPUT VOLTAGE

- INRUSH CURRENT: 60/100A @ 115/230VAC (25℃)

- POWER FACTOR CORRECTION: 95% @ 110V, FULL LOAD

OUTPUT CHARACTERISTICS:

| OUTPUT VOLTAGE | OUTPUT CURRENT |  | REGULATION |  | OUTPUT |
| --- | --- | --- | --- | --- | --- |
|  | MIN. [A] | MAX. [A] | LOAD | LINE | RIPPLE & NOISE MAX. [P-P] |
| 5V | 4.0 | 48 | ± 5% | ± 50mV | 70mV |
| 12V | 5.0 | 50 | ± 6% | ± 50mV | 120mV |
| -5V | 0.2 | 1 | +5%, -10% | ± 50mV | 120mV |
| -12V | 0.2 | 1.5 | +5%, -10% | ± 50mV | 120mV |
| 3.3V | 4.0 | 45 | ± 5% | ± 50mV | 70mV |
| +5VSB | 0.4 | 3.5 | +5%, -6% | ± 50mV | 70mV |

REMARKS:

- THE OUTPUT POWER OF 5V & 3.3V MAX: 40A

2.  EACH POWER MODULE OUTPUT MAX: 420W

3.  TOTAL OUTPUT POWER MAX: 760W / 800W

SPECIFICATION:

- TEMPERATURE RANGE: OPERATING: 0℃ --- 40℃

- STORAGE:  -20℃ --- 80℃

- HOLD UP TIME: 16 ms MINIMUM AT FULL LOAD & NORMAL INPUT VOLTAGE

- DIELECTRIC WITHSTAND: INPUT / OUTPUT 3000 VAC FOR 1 SECOND

- INPUT TO FRAME GROUND 1500 VAC FOR 1 SECOND

- EFFICIENCY: 65% TYPICAL AT 115VAC FULL LOAD

- POWER GOOD SIGNAL: ON DELAY 100 ms TO 500 ms, OFF DELAY 1 ms

- OVER POWER PROTECTION: 110% ~ 180%

- OVER VOLTAGE PROTECTION: +5V  5.7V ~ 6.5V, 3.3V  3.9V ~ 4.7V

- +12V  13.3V ~ 14.3V

- OVER CURRENT PROTECTION: 110% ~ 180%

- SHORT CIRCUIT PROTECTION: +5V, -5V, +12V, -12V, +3.3V

- EMI NOISE FILTER: FCC CLASS A, CISPR22 CLASS A

- SAFETY: UL 1950, CSA 22.2 NO/ 950, TÜV IEC 950

- REMOTE ON / OFF CONTROL

- THE UNIT SHALL ACCEPT A LOGIC OPEN COLLECTOR LEVEL WHICH WILL DISABLE / ENABLE ALL THE OUTPUT VOLTAGE (EXCLUDE +5V STANDBY),

- AS LOGIC LEVEL IS LOW, OUTPUTS VOLTAGE WERE ENABLE,

- AS LOGIC LEVEL IS HIGH, OUTPUTS VOLTAGE WERE DISABLE.

- 3.3V REMOTE SENSING

- DIMENSION: 265 (D) x 101 (W) x 125 (H) mm

INPUT CHARACTERISTICS:		                      M1Z4-5E85V3H

- VOLTAGE: 90 ~ 264 VAC FULL RANGE.

- FREQUENCY: 47 ~ 63 Hz.

- INPUT CURRENT: 9A (RMS) FOR 230 VAC

- 22A (RMS) FOR 115 VAC

- INRUSH CURRENT: 35A MAX. FOR 115 VAC PER MODULE

- 40A MAX. FOR 230 VAC PER MODULE

- POWER FACTOR CORRECTION: PFC CAN REACH THE TARGET OF 95% AT 115/230VAC, FULL LOAD.

- OUTPUT CHARACTERISTICS:

| OUTPUT VOLTAGE | OUTPUT CURRENT(A) |  | REGULATION |  | OUTPUT |
| --- | --- | --- | --- | --- | --- |
|  | MIN. | MAX. | LOAD | LINE | RIPPLE & NOISE MAX.[P-P] |
| +5V | 2 | 64 | ±5% | ± 1% | 70mV |
| +12V | 3 | 120 | ±5% | ± 1% | 120mV |
| -12V | 0 | 1.2 | ±5% | ± 1% | 120mV |
| +3.3V | 0 | 64 | ±5% | ± 1% | 70mV |
| +5VSB | 0 | 6.0 | ±5% | ± 1% | 70mV |

TOTAL OUTPUT POWER 1485W

SPECIFICATION:

- TEMPERATURE RANGE: OPERATING 00C --- 500C, STORAGE –200C --- 800C

- HOLD UP TIME: 16 ms MINIMUM AT FULL LOAD & NORMAL INPUT VOLTAGE

- EFFICIENCY: 78% TYPICAL AT 115VAC FULL LOAD

- POWER GOOD SIGNAL: ON DELAY 100 ms TO 500 ms, OFF DELAY 1 ms

- OVER POWER PROTECTION: 110~160%

- OVER VOLTAGE PROTECTION: +5V→5.7V~6.5V, +3.3V→4.0V~5.7V, +12V→14.3V~17.3V

- OVER CURRENT PROTECTION: +5V, +12V, +3.3V

- SHORT CIRCUIT PROTECTION: +5V, +3.3V, +12V, -12V, +5VSB

- SAFETY: TO MEET UL, CB, TUV

- EMI NOISE FILTER: FCC CLASS A, CISPR22 CLASS A

- DIMENSION: 310 (D) x 422 (W) x 43 (H) mm

  - INSTALLATION & TESTING

Mount the power system into the system chassis

Attach the connectors to main board by following the main board’s instructions, there are various on pinouts / connectors in both the power system and main board, they

should match each other, otherwise the connection will cause undetectable harms.

Attach all the remaining power supply connections to the various peripherals as

needed, these connectors maybe “keyed”, so there will be only one possible way to connect them.

Before applying power source to the system, make sure these are no loose or incorrect connections. Please check your power system is AC source version or DC

source version, to supply the correct source.

To test the redundancy function, please supply the source to the individual power modules. If the individual power module. Operates normally, the LED on the module lits in GREEN, and the external warning LED also lits in GREEN. Now remove the source from one of the individual power module, the warning buzzer in the power system will sound, and the external warning LED which displays the status of the total power supply system will blink/RED, the individual LED indicating the power module’s status will not light. Meanwhile the power system will continue to backup the power output without affecting the system’s operation.

The warming buzzer will continue sounding, the user can reset the warning buzzer by pressing the buzzer reset switch.

Turn on the power module which is turned off for testing earlier, the sound of the warning buzzer will disappear, the external warning LED will turn GREEN again; the LED indicating the status of power module will light again, you may test other power module by performing the similar procedure.

  - Hot-swap procedures

Please refer to the following when one power module is found defective.

(1) Locate the defective power module by examining the individual LED (if LED is without light, it indicates the power module is defective).

WARNING:

Please perform the BELOW step carefully; otherwise, it may cause shut down of the whole system.

(2) Turn off

WARNING:

Please do not remove the defective power module until you have worn gloves to keep from been burned. This is due to the cover of the power module is used as heat sink for cooling. Usually, its temperature is around 50-60 degree Celsius under full load condition.

(3) Remove the defective power module by puling out method.

WATNING:

Please put aside the power module to wait for cooling down. Keep other people from toughing it until it is cooled.

(4) Replace a new / GOOD power module, insert the power module into the power system till to the end.

(5) Turn on the new power module.

(6) Check the LED of the power module light GREEN.

(7) Check the LED which indicates the total power system status, that SHOULD be

from blink/RED to GREEN.

(8) If you want to test this new power module and simulate the defective situation, please refer to Section 1.7 Installation & Testing Section.

  - PINOUTS AND FUNCTION OF THE CONNECTORS

A.  Power module defective signal:

PIN#     VOLTAGE     SPECIFICATION

1     GND

2     TTL SIGNAL   pull up to +5Vsb

Low Active --- Defective

High      --- Normal

B.  Power status LED:

PIN#     VOLTAGE     SPECIFICATION

1     GND

2     12V           Resistance 1K ohm to +12V

Low Active(blink)  --- Defective

High      (Green) --- Normal

C.  Buzzer reset switch:

PIN#     VOLTAGE     SPECIFICATION

2     GND

1     5V            pull up to +5Vsb

Low Active --- on shoot trigger

TTL signal:

Sink current max. 5mA

Source current max. 50uA

Low Active  ---Defective

High        ---Normal

  - TROUBLE SHOOTING

If you have followed all directions correctly, these should be no problem. Some common symptoms are: the system doesn’t work, buzzer sound, work for a very short period etc., please try the following steps to verify and correct it:

1. Check all the connections (correct pinouts, loose connection, wrong direction etc.,)

2. Check for short-circuit or defective peripherals by unhooking each peripheral once at a time. When the system functions again, you have solved the problem.

3. Once you hear the buzzer sound or see the LED is blinking/ RED, please aware of:

a. If the source is OK.

b. If the load is under the minimum / over. The maximum load of each channel

(please refer the Specification)

c. If Ac / Dc input voltage been selected correctly.

d. If the power cable(s) been well plugged into the Input kit.

Suppose the above condition been happened, please turn off the power system,

await for 2-3 minutes for releasing the protection state, then test it again.

e. If buzzer still sound or the LED shows power module is defective, please locate which power module is defective, perform Hot-swap procedure at your proper time, send the defective item to your vendor for RMA operation.

f. If you can not fix the problem, please contact with your vendor for supporting.

The description stated herein is subject to change without prior notice.

All brand names and trademarks are the property of their respective owners.